Regn No: _________________

Name: ___________________

(To be written by the candidate)

9TH NATIONAL CERTIFICATION EXAMINATION– December, 2009

FOR

ENERGY AUDITORS

PAPER – 4: Energy Performance Assessment For Equipment and Utility Systems Date: 20.12.2009 Timings: 1400-1600 HRS Duration: 2 HRS Max. Marks: 100

General instructions:

- Please check that this question paper contains 8  printed pages

- Please check that this question paper contains 16 questions

- The question paper is divided into three sections

- All questions in all three sections are compulsory

- All parts of a question should be answered at one place

# Section - I: 	  SHORT DESCRIPTIVE QUESTIONS			Marks: 10 x 1 = 10

(i)	Answer all Ten questions

- Each question carries One mark

| S-1 | A cogeneration plant with a back pressure turbine has a constant steam demand and fluctuating power demand. What is the common option to meet the fluctuating power demand? Ans Parallel operation with grid |
| --- | --- |
| S-2 | What are the two major sources of waste heat available from a water-cooled Diesel Generator set? Ans Exhaust flue gases and jacket cooling water |
| S-3 | For determining heat loss in flue gases due to incomplete combustion which flue gas constituent needs to be measured? Ans Carbon monoxide |

| S-4 | Which parameter needs to be measured to assess the percentage loading of a motor by slip method neglecting voltage correction? Ans Motor speed |
| --- | --- |
| S-5 | How many volt-amperes (VA) does a 100 Watt incandescent light require? Ans 100 VA |
| S-6 | In the indirect method of boiler efficiency evaluation, list any two additional losses computed for solid fuel fired boilers as compared to liquid and gas fired boilers? Ans. Unburnt losses in fly ash (Carbon) Unburnt losses in bottom ash (Carbon) |
| S-7 | Why do biomass combustion projects qualify for CDM benefits even though they emit carbon dioxide? Ans: Because it absorbs the same amount of carbon in growing as it releases when consumed as fuel Or Biomass is carbon neutral |
| S-8 | Name two most common bio fuels used for transportation Ans 1. Biodiesel 2. Ethanol |
| S-9 | Which loss is assumed in the determination of electric motor efficiency? Ans The stray load loss is estimated and not measured for testing electric motor efficiency. |
| S-10 | In a shell and tube heat exchanger, engaged in heat transfer between fouling fluid and clear fluid, the fouling fluid should be put on shell side or tube side? Ans Tube side |

…………. End of Section - I ………….

# Section - II: 	  LONG DESCRIPTIVE QUESTIONS                		Marks: 2 x 5 = 10

(i)	Answer all Two questions

(ii)	Each question carries Five marks

L-1   	The steam flow to a process plant is 5000 kg/hr. 2000 kg/hr of condensate at 173oC is returned to boiler feed water tank due to its own pressure. However there is 10% heat loss in transit to boiler feed tank. The balance is made up as feed water at 30oC. The final feed water temperature observed was 95oC. Comment on the feed water temperature. The plant personnel are sure that the temperature gauge is in order.

Ans	Heat in condensate (less 10%) + Heat in make up water =  Heat in feed water

2000 X 173 X 0.9 + 3000 X 30  =  5000 X Tf

311400 + 90000  =  5000 X Tf

Tf  =	80.28oC

(3 Marks)

The feed water temperature cannot be more than 80.28oC. The high temperature of 95oC is mostly due to live steam leakage, as the temperature gauge is OK.

(2 Marks)

L-2	The maximum demand registered by an automobile plant is 5000 KVA and the power factor is 0.95. The plant management converts the existing electrical resistance heated furnace with an average load of 750 kW to gas heating as a cost reduction measure. What will be effect on maximum demand and power factor with this conversion?

Ans.	Registered maximum demand	=	5000 KVA

Electrical load (real power)		=	5000 X 0.95

=	4750 KW

KVAR2		=	KVA2 – KW2

KVAR2		=	(5000)2 – (4750)2

KVAR		=	100	(502) – (47.5)2

=	1561

(3 Marks)

KVAR in the system will remain same.

Reduction in real power by conversion is 750 KW.

Real Power	=	4750 – 750  =  4000 KW

KVA2		=	KW2 + KVAR2

=	(4000)2 + (1561)2

KVA		=	4294

Power factor	=	4000 / 4294  =  0.932

Reduction in Electrical Demand	=	5000 – 4294

=	706 KVA

Reduction in Power Factor		=	0.95 – 0.932

=	0.018

(2 Marks)

…………. End of Section - II ………….

# Section - III: 	   NUMERICAL QUESTIONS 		    		Marks: 4 x 20 = 80

(i)	Answer all Four questions

(ii)	Each question carries Twenty marks

N -1	Given below is a set of curves for a centrifugal fan. At its Best Efficiency Point (BEP) determine to the nearest approximation the following:

- Static pressure in mmwc

- Flow in m3/hr

- Shaft power in kW

- Work out  the static efficiency of the fan by calculation

- Power drawn by the motor if the motor operating efficiency is 90%

Ans

| Static pressure in inches H2O | 36 |
| --- | --- |
|  | (2 Marks) |
| Static pressure in mmwc | 914.4 mmwc |
|  | (2 Marks) |
| Flow in CFM | 2750 |
|  | (2 Marks) |
| Flow in m3/hr | 4672.28 m3/hr ie 1.3 m3/sec |
|  | (2 Marks) |
| Shaft power in hp | 29 |
|  | (2 Marks) |
| Shaft power in kW | 21.6 kW |
|  | (2 Marks) |
| Fan Efficiency | Q x dP/(102 x kW) |
|  | 1.3 x 914.4 /(102 x 21.6) |
|  | 54 % |
|  | (5 Marks) |
| Motor input power at 90% | 21.6 / 0.9 |
|  | = 24 kW |
|  | (3 Marks) |

The data is read from the graph and hence a deviation of +/- 10% in values may be given full marks.

N-2    	In a Continuous Process Industry 5 Tonne per hour hot oil on process stream has to be cooled from 230oC to 110oC by DM water at 25oC heated to 80oC on its route to boiler de-arator.

- Depict the heat exchange process on a schematic for both parallel and counter flow heat exchanger clearly indicating inlet and outlet temperature and terminal temperature difference.

- Find out LMTD for parallel and counter flow heat exchangers and comment on the preference of the heat exchanger.

- Find out the DM water flow rate through the heat exchanger. Assume specific heat of hot oil to be 0.5 kCal / kgoC.

Ans.

Hot Oil						Hot Oil

230oC				  110oC	    230oC			   110oC

Parallel Flow

TTD				  TTD		   TTD              Counter Flow     TTD

t1 = 205                                      t2 = 30  	    t1 = 150oC  			       t2 = 85

25oC				    80oC	    80oC			   25oC

Cold DM Water							Cold DM Water

t1 -         t2

LMTD parallel flow    =     ------------------------

Ln       t1 /       t2

205 - 30

=     ------------------	=	91.15oC

Ln  205 / 30

(8 Marks)

t1 -         t2

LMTD counter-flow  =     ------------------------

Ln       t1 /       t2

150 - 85

=     ------------------	=	114.44oC

Ln  150 / 85

(8 Marks)

Counter flow heat exchanger is preferred as the LMTD is larger and hence heat exchanger area will be less and compact.

Mc X 1 X  (80 – 25)  = mh X Cph X (230 – 110)

Mc 	= 	5000 X 0.5 X (230 – 110) / 55

=	5454.54 Kg / hr

DM water flow rate	=	5454.54 Kg / hr

(4 Marks)

N-3    	The following are the data collected for a boiler using furnace oil as the fuel. Determine the boiler efficiency based on GCV by indirect method ignoring radiation and convection losses.

Ultimate chemical analysis (% weight) :   Carbon : 84, Hydrogen : 12,  Nitrogen : 0.5, Oxygen : 1.5, Sulphur : 1.5, Moisture : 0.5, GCV of fuel 10,397 kCal/kg and humidity  0.015 kg moisture/kg of dry air.

Flue gas analysis: CO2 : 12% volume,  flue gas temperature : 180oC and ambient temperature : 20oC

Ans:

a) Theoretical Air = 11.43 x 0.84 + 34.5 x (0.12 – 0.015/8) + 4.32 x 0.015 = 13.74

(or)

Theoretical Air = 11.6 x 0.84 + 34.8x (0.12 – 0.015/8) + 4.35 x 0.015 = 13.92

(2 Marks)

b) Theoretical % CO2 	= Moles of C/(Moles of N2 + Moles of C + Moles of Sulphur)

= 100 x (0.84/12)/(13.74 x 0.77/28 + 0.005/28 +0.84/12 + 0.015/32) = 		15.62%

(or)

Theoretical % CO2 	= Moles of C/(Moles of N2 + Moles of C + Moles of Sulphur)

= 100 x (0.84/12)/(13.92 x 0.77/28 + 0.005/28 +0.84/12 + 0.015/32) =  15.44%

(2 Marks)

Depending on the variation in the above values (a and b) the subsequent calculations will also have a minor variation in the end result, which can be ignored.

c) Excess air supplied = 7900 x(15.62 -12)/(12(100-15.62)) = 		28.24%

(2 Marks)

d) Actual mass of air supplied = (1+0.2824) x 13.74 = 		17.62 kg/kg of oil.

(2 Marks)

e) Actual mass of dry flue gas =

0.84 x 44/12 + 0.005 + 17.62 x 0.77 + 0.015 x 64/32 + 3(17.62-13.74) x 0.23

= 19.3596 kg/kg oil

(2 Marks)

f) % loss by dry flue gas = 19.3596 x 0.23 x (180-20)/10,397 = 0.0685 or 6.85%

(2 Marks)

g) % loss by formation of water from Hydrogen in the fuel

9 x 0.12 x (584 + 0.45 (180-20))/10,397 = 0.681 or				6.81%

(2 Marks)

h) % loss due to moisture in fuel = 0.005 x (584 +0.45 (180-20))/10,397 = 	0.03%

(2 Marks)

i) % loss due to moisture in air = 17.62 x 0.015 x 0.45 (180-20)/10,397 = 0.183%

(2 Marks)

j) Boiler efficiency = 100- 6.85 – 6.81 – 0.03 – 0.183 = 			86.127%.

(2 Marks)

N-4	A process plant is installing a 5 MW gas turbine cogeneration system with 12 TPH waste heat boiler to meet the power and steam demand of the plant. The plant will operate at 90% of capacity, meeting the entire power requirement of the plant, which is presently drawn from grid supply. The co-gen plant will also meet the steam requirement of 10 TPH, which is presently generated in a gas fired boiler with 86% efficiency on N.C.V. basis. Calculate the differential cost between cogenerated power and grid power per unit and also the additional natural gas requirement per day based on the following data.

Capacity of gas turbine			=	5000 kW

Plant load factor				=	90%

Auxiliary power consumption			=	1%

Operating hrs. per annum			=	8000

Net calorific value of natural gas		=	9500 kCal / Sm3

Cost of natural gas				=	Rs.8 / Sm3

Steam produced by co-gen waste heat	=	10 TPH boiler

Annual expenditure towards	depreciation

and interest					=	Rs 500 lacs

Annual expenditure for operation &

maintenance of co-gen plant			=	Rs 200 lacs

Heat Rate of gas turbine on NCV		=	3050 kCal / kWh

Cost of electric power from grid supply	=	Rs. 4.5/ kWh

Enthalpy of steam				=	665 kCal/ kg

Feed water temperature			=	85oC

Ans	Power generation from cogen plant	=	5000X 0.9 X 8000  =  360 lac Kwh

Auxiliary power				=	1%

Net power generation			=	0.99 X 360  =  356.4 lac Kwh

Natural gas requirement for		=	360 X 3050 / 9500 = 115.57 lac Sm3

power generation

(4 Marks)

Cost of fuel per annum		=	115.57 X 8  =  Rs.924.56 lacs

Annual expenditure for interest,	=	500 + 200  =  700 lacs

depreciation and O&M

Total cost of generation		=	Rs.1624.56 lacs.

Cost of cogeneration power		=1624.56 X 105 / 356.4 X 105

=Rs.4.56 / Kwh.

(4 Marks)

Gas consumption in existing gas	=	[10000 (665 – 85) / (0.86 X 9500)]

fired boiler			=	710 Sm3/hr

=	17040 Sm3/day

Cost of steam 			=	710*Rs. 8/10

=	Rs. 568/Ton

Annual savings by avoiding steam=	10 X 568 X 8000

In the existing gas fired Boiler	=	Rs. 454.4 Lacs.

Cost of generation after giving	=	1624.56 – 454.4  =  Rs.1170.16 lacs

credit for steam generation

Cost of generation after accounting =	1170.16 X 105 / 356.4 X 105

for steam cost

=  	Rs. 3.28 / Kwh

(5 Marks)

Grid power cost			=	Rs. 4.5 / Kwh

Cost advantage for cogen plant	=	4.5 – 3.28  =  Rs.1.22 / Kwh

generation

Daily gas requirement for operating	=	5000 X 0.9 X 3050 X 24

GT cogen plant				          9500

=	34673.68 Sm3 / day

(3 Marks)

Additional gas requirement for 	=	34673.68 – 17040  =  17633.68 Sm3/day

co-gen plant

(4 Marks)

-------- End of Section - III ---------

# Text boxes

Shaft power (HP)